## Sheet1
Instructions on how to test the remote reset of our WIC installations
Last updated on 28.01.2015
by R. Mompo | [5 empty] | Login to cerntsbe10
Open Putty (in the Start-Bar of Windows)
Connect to cs-ccr-dev1
Login as yourself in the black terminal that will appear
Type: cd /mcr/reset
|  | Rack name for TWIDO system: CYFRE01 |  |  |  | type: ./rem_reset PLC_name (whereas PLC_name can be found in netops DB, typically it is something like cfp-ua23-ciwlr2). | [6 empty] | Important: Entrer PLC name in lower case!
|  | Reboot host name | Twido | canal |  | Machine: | PLC name: | IP address: | Location: | Safety: | Redundant PS: | Beam Dump: | "Remote reset": | Remote Reset cable id.:
declaration ok | cable connecté | cfp-150-ciwleir1 | cfp-150-crr1 | 4 | 1 | LEIR | cfp-150-ciwleir1 | 172.18.231.234 | 0150 R-0001 | Yes | Yes | No | Ok | 2609079A | Request "Remote reset" for other racks: MYUD Ring: 2609078A, MYUD Ligne: 2609077A, RA027(bat. 250): 2609076A
declaration ok | cable connecté | cfp-351-ciwlinac3 | cfp-363-crr1 | 8 | 2 | Linac 3 | cfp-351-ciwlinac3 | 172.18.226.198 | 0351 R-0001 | Yes | Yes | No | Ok | 2703565A
declaration ok | cable connecté | cfp-ba4-ciwtt40 | cfp-ba4-crr1 | 16 | 3 | TT40 | cfp-ba4-ciwtt40 | 172.18.195.91 | 0871 R-0009 ( Zone: RA1350 ) | No | No | Yes | Ok | 3406364A | Test ok with a short on place
declaration ok | cable connecté |  |  |  | 4 | TT41 (CNGS) | cfp-bb4-ciwtt41 | 172.18.195.180 | 0921 R-0010 ( Zone: EYY1116 ) | No | No | Yes | Ok | 3405247A
declaration ok | cable connecté | cfp-ba6-ciwtt60 | cfp-ba6-crr1 | 14 | 5 | TT60 | cfp-ba6-ciwtt60 | 172.18.196.179 | 0873 R-0010 ( Zone: RA 1866 ) | No | No | Yes | Ok | 3602205A | Test ok with a short on place. Signal name to be modified.
declaration ok | cable connecté |  |  |  | 6 | TT66 (BA6) HiRadMat | cfp-ba6-ciwtt66 | 172.18.196.150 | 0873 R-0010 | Yes | Yes | Yes | Ok | 3602427A
declaration ok | cable connecté |  |  |  | 7 | TT66 (BA7) HiRadMat | cfp-ba7-ciwtt66 | 172.18.196.206 | 0876 R-0001 | Yes | Yes | Yes | Ok | 3702730A
[5 empty] | 8 | SPS TT20 | wic1ba2 | 172.18.194.96 | 0869 R-0001 ( Zone: RA4238 ) | No | No | No |  | No cable | Prototype installation without the remote test feature
declaration ok | cable connecté | cfp-us15-ciwlr1 | cfp-us15-crr1 | 29 | 9 | LHC P1 | cfp-us15-ciwlr1 | 172.18.37.213 | 2127 1-3607 | Yes | Yes | Yes | Ok | 1125227 | Test ok with a short on place
declaration ok | cable connecté | cfp-ua23-ciwlr2 | cfp-ua23-crr1 | 32 | 10 | LHC P2 | cfp-ua23-ciwlr2 | 172.18.63.232 | 2218 R-0000 ( Zone: MYWIC01 ) | Yes | Yes | Yes | Ok | 1218958 | Test ok with a short on place
declaration ok | cable connecté |  |  |  | 11 | LHC P3 | cfp-uj33-ciwlr3 | 172.18.60.162 | 2313 R-0000 ( Zone: UJ33 ) | Yes | Yes | Yes | Ok | 1310428
declaration ok | cable connecté | cfp-ua47-ciwlr4 | cfp-us45-crr1 | 20 | 12 | LHC P4 | cfp-ua47-ciwlr4 | 172.18.46.42 | 2439 RA-0000 ( Zone: RACK MYWIC01 ) | Yes | Yes | Yes | Ok | 1424076 | Test ok with a short on place
declaration ok | cable connecté | cfp-usc55-ciwlr5 | cfp-ul55-crr1 | 29 | 13 | LHC P5 | cfp-usc55-ciwlr5 | 172.18.53.159 | 3524 1-0000 ( Zone: RACK MYWIC01 ) | Yes | Yes | Yes | Ok | 1517091A | Test ok with a short on place
declaration ok | cable connecté |  |  |  | 14 | LHC P6 | cfp-us65-ciwlr6 | 172.18.40.104 | 2627 1-0000 ( Zone: RACK MYWIC01 ) | Yes | Yes | Yes | Ok | 1619685A
declaration ok | cable connecté | cfp-tz76-ciwlr7 | cfp-tz76-crr1 | 1 | 15 | LHC P7 | cfp-tz76-ciwlr7 | 172.18.57.112 | 2743 0A-0000 | Yes | Yes | Yes | Ok | 1701070A | The cable id. 1701067A is also coming in the rack? Test ok with a short on place
declaration ok | cable connecté | cfp-ua83-ciwlr8 | cfp-ua83-crr1 | 7 | 16 | LHC P8 | cfp-ua83-ciwlr8 | 172.18.34.200 | 2818 RA-0000 | Yes | Yes | Yes | Ok | cable rack a rack | 1813908 arrive en US851 à déposer. Le rack en UA83 est mal nommé MYWPC au lieu de MYWIC01. Test ok with a short on place.
declaration ok | cable connecté |  |  |  | 17 | TI2 | cfp-ba7-ciwti2 | 172.18.196.233 | 0876 R-0001 ( Zone: BA7 / 2007 ) | No | No | Yes | Ok | ? | 3701964A ou 3702122A ?
declaration ok | cable connecté | cfp-ba4-ciwti8 | cfp-ba4-crr1 | 14 | 18 | TI8 | cfp-ba4-ciwti8 | 172.18.195.104 | 0871 R-0009 ( Zone: RA1350 ) | No | No | Yes | Ok | 3405246A | Test ok with a short on place. BNC cable 3405246A replaced in december 2014.
declaration ok | cable connecté | cfp-361-ciwmains | cfp-361-crr1 | 25 | 19 | Booster Mains | cfp-361-ciwmains | 172.18.233.19 | 0361 1-0012 (Rack N637) | Yes | Yes | Yes | Ok | 2724847A | A trigger sent to the Mains will reboot Mains + Aux1 (as PS is common for Mains and Aux1 PLCs).
declaration ok | cable connecté | cfp-361-ciwmains | cfp-361-crr1 | 25 | 20 | Booster Aux1 | cfp-361-ciwbaux1 | 172.18.228.106 | 0361 1-0012 | Yes | Yes | Yes | Ok | 2724847A | A trigger sent to the Mains will reboot Mains + Aux1 (as PS is common for Mains and Aux1 PLCs).
declaration ok | cable connecté | cfp-361-ciwbaux3 | cfp-361-crr1 | 26 | 21 | Booster Aux2 | cfp-361-ciwbaux2 | 172.18.233.14 | 0361 1-0012 ( Zone: RACK N635 ) | Yes | Yes | Yes | Ok | 2724848A | A trigger sent to the Aux3 will reboot Aux2 + Aux3 (as PS is common for Aux2 and Aux3 PLCs)$.
declaration ok | cable connecté | cfp-361-ciwbaux3 | cfp-361-crr1 | 26 | 22 | Booster Aux3 | cfp-361-ciwbaux3 | 172.18.233.13 | 0361 1-0012 | Yes | Yes | Yes | Ok | 2724848A | A trigger sent to the Aux3 will reboot Aux2 + Aux3 (as PS is common for Aux2 and Aux3 PLCs)$.
| demande de cable à faire |  |  |  | 23 | Linac 4 | cfp-400-ciwlinac4 | 172.18.238.227 | 0400 1-0001 ( Zone: RA: MYWIC01 ) | Yes | Yes | Yes |  | No cable
| demande de cable à faire |  |  |  | 24 | Linac 4 TL | cfp-400-ciwtln4 | 172.18.239.31 | 0400 1-0001 ( Zone: RA: MYWIC02 ) | Yes | Yes | Yes |  | No cable
declaration ok | cable connecté | cfp-868-ciwspsba1 |  |  | 25 | SPS BA1 | cfp-868-ciwspsba1 | 172.18.204.98 | 0868 R-1207 ( Zone: RA2337 ) | Yes | Yes | Yes | Ok | 3102585A
declaration ok | cable connecté | cfp-869-ciwspsba2 |  |  | 26 | SPS BA2 | cfp-869-ciwspsba2 | 172.18.212.172 | 0869 R-0001 ( Zone: RA2338 ) | Yes | Yes | Yes | Ok | 3202315A
declaration ok | cable connecté | cfp-870-ciwspsba3 |  |  | 27 | SPS BA3 | cfp-870-ciwspsba3 | 172.18.194.152 | 0870 R-0009 ( Zone: RA1777 ) | Yes | Yes | Yes | Ok | 3305207A
declaration ok | cable connecté | cfp-905-ciwspsbb3 |  |  | 28 | SPS BB3 Ring-Line | cfp-905-ciwspsbb3 | 172.18.195.22 | 0905 R-0001 ( Zone: RA8518 ) | Yes | Yes | Yes | Ok | 3305208A
declaration ok | cable connecté | cfp-871-ciwspsba4 |  |  | 29 | SPS BA4 | cfp-871-ciwspsba4 | 172.18.214.220 | 0871 R-0009 ( Zone: RA2502 ) | Yes | Yes | Yes | Ok | 3406361A
declaration ok | cable connecté | cfp-872-ciwspsba5 |  |  | 30 | SPS BA5 | cfp-872-ciwspsba5 | 172.18.199.232 | 0872 R-0009 ( Zone: RA1108 ) | Yes | Yes | Yes | Ok | 3502097A
declaration ok | cable connecté | cfp-873-ciwspsba6 |  |  | 31 | SPS BA6 | cfp-873-ciwspsba6 | 172.18.205.86 | 0873 R-2509 ( Zone: RA2337 ) | Yes | Yes | Yes | Ok | 3602722A
| demande EN-EL en cours |  |  |  | 32 | Hie-Isolde | cfp-170-ciwhiso1 |  |  | Yes | Yes | No |  | No cable
| demande EN-EL en cours |  |  |  | 33 | Hie-Isolde | cfp-170-ciwhiso2 |  |  | Yes | Yes | No |  | No cable
In bold: info retreived from GESMAR
Note on H10: Richard Mompo: Device name and Interface name should be identical on Netops.
Note on M10: For non safety installation the PC status is NOT taken into account for the generation of the Beam Dump signal.
Note on N11: Richard Mompo: Not all 24DI modules are defined from WINCC to do a ACK PASS (button not active when pressing select. In case of a passivation on 1 of these modules an access to the machine is needed to do a ON/OFF of the rack BEFORE doing a ON/OFF of the PLC.
Note on N12: Richard Mompo: ACK PASS feature form WinCC: Tested ok for each 24DI module (29.10.14).
Note on E23: rmompo: Intervention Yan & Christophe le 03.12.2014: Notre cable "1517091A" été trouvé branché sur la sortie 25. Yan l'a déplacé sur la sortie 29, comme défini dans le fichier d'Emmanuel (sortie qui était libre) et maintenant ça marche!
Note on M29: Not connected on a CIBU yet.
Note on M30: Not connected on a CIBU yet.
Note on M31: Not connected on a CIBU yet.
Note on M32: Not connected on a CIBU yet.